## GC
General Information |  | ICONS | Value | Description | [6 empty] | Units
Model Name | PSSECOMM | M | 1 | Type of signals to send (0 - VARs; 1 - STATEs) | [6 empty] | -
Author | Tin Rabuzin | M+1 | 1 | Starting index of VARs/STATEs that will be transferred | [6 empty] | -
PSSE Version | PSSE Version (35) | M+2 | 6 | Number of VARs/STATEs that will be transfered starting from those indexed by ICON(M) | [6 empty] | -
User Model | SGGC0100 | M+3 | 1 | Starting index of VARs where received signals will be written | [6 empty] | -
ICONs | 5 | M+4 | 2 | Number of received VARs
CONs | 0 | [9 empty] | -
STATEs | 0 | [9 empty] | -
VARs | 50 | [9 empty] | -
-
-
DYRE Data
/ PSSECOMM PSSE Version (35)
MINS 'USRMSC' 'PSSECOMM' 512 0 5 0 0 50
1 1 6 1 2
/
|  |  |  | CONs | Value | Default Value | Min | Max | Parameter Name | Description | Units
|  |  |  | J | 3.625 |  |  |  | WTBASE | Rated power of the WTG
|  |  |  | J+1 | 1 |  |  |  | APC_P_lim | APC saturation limit.
|  |  |  | J+2 | 1 |  |  |  | CosPhiControl_Tfilt_p_act | Time constant to filter P used in Cosphi & Cosphi_P control modes.
|  |  |  | J+3 | 0.1 |  |  |  | DipMaxTime_PCC | Time to deactivate the WFR dip mode after POC voltage is recovered above Vdip_off_threshold_PCC.
|  |  |  | J+4 | 5 |  |  |  | FastRamp_TimeUp | Maximum time to increase P to the required value, when using Fast Freq Ramps.
|  |  |  | J+5 | 2 |  |  |  | FastRamp_TimeDw | Maximum time to decrease P to the required value, when using Fast Freq Ramps.
|  |  |  | J+6 | 0.0001 |  |  |  | Freq_SensibilityBand | Freq Sensibility Band to consider that the freq has changed and a new Pref is calculated.
|  |  |  | J+7 | -0.022222 |  |  |  | K_RRLf_balance | Active power falling ramp of 1 WTG for Balance control mode. By default, -100kW/s.
|  |  |  | J+8 | 0.016667 |  |  |  | K_RRLr_balance | Active power rising ramp of 1 WTG for Balance control mode. By default, 75kW/s.
|  |  |  | J+9 | 0.22 |  |  |  | Kp_APC_P | APC Controller proportional gain.
|  |  |  | J+10 | 0.1 |  |  |  | OVMaxTime_PCC | Time to deactivate the WFR OV mode after POC voltage is recovered above Vov_off_threshold_PCC.
|  |  |  | J+11 | 0.03 |  |  |  | PDist_BandPct | Parks Band value for the error to multiply the Preference. Normally 0.01-0.05 pu.
|  |  |  | J+12 | 5 |  |  |  | PDist_nRepCycles | Number of cycles in which the reference in repeated. By default: Fast Arch. --> 10; Standard Arch. --> 4.
|  |  |  | J+13 | 49.5 |  |  |  | PDistPushBand | Push band to change from Fast to Slow ramping in the Pdistribution.
|  |  |  | J+14 | 16.5 |  |  |  | PDistResetBand | Max band of difference between setpoint and measurent to Reset setpoint in PDistribution
|  |  |  | J+15 | 330 |  |  |  | PDistS1FastRamp | Fast Ramp value used in Pdistributor
|  |  |  | J+16 | 330 |  |  |  | PDistS1SlowRamp | Fast Ramp value used in Pdistributor
|  |  |  | J+17 | 0.05 |  |  |  | PDistThrottle | Throttle step from measurement to sustain the WF production
|  |  |  | J+18 | -0.050283 |  |  |  | PF_curve_f_1 | P-f curve frequency deviation points. Defined by 10 monotonically increasing points.
|  |  |  | J+19 | -0.050283 |  |  |  | PF_curve_f_2 | P-f curve frequency deviation points. Defined by 10 monotonically increasing points.
|  |  |  | J+20 | -0.050283 |  |  |  | PF_curve_f_3 | P-f curve frequency deviation points. Defined by 10 monotonically increasing points.
|  |  |  | J+21 | -0.000283 |  |  |  | PF_curve_f_4 | P-f curve frequency deviation points. Defined by 10 monotonically increasing points.
|  |  |  | J+22 | 0 |  |  |  | PF_curve_f_5 | P-f curve frequency deviation points. Defined by 10 monotonically increasing points.
|  |  |  | J+23 | 0.000283 |  |  |  | PF_curve_f_6 | P-f curve frequency deviation points. Defined by 10 monotonically increasing points.
|  |  |  | J+24 | 0.047783 |  |  |  | PF_curve_f_7 | P-f curve frequency deviation points. Defined by 10 monotonically increasing points.
|  |  |  | J+25 | 0.047783 |  |  |  | PF_curve_f_8 | P-f curve frequency deviation points. Defined by 10 monotonically increasing points.
|  |  |  | J+26 | 0.047783 |  |  |  | PF_curve_f_9 | P-f curve frequency deviation points. Defined by 10 monotonically increasing points.
|  |  |  | J+27 | 0.047783 |  |  |  | PF_curve_f_10 | P-f curve frequency deviation points. Defined by 10 monotonically increasing points.
|  |  |  | J+28 | 1 |  |  |  | PF_curve_P_1 | P-f curve active power points. Defined by 10 points. They are multiplied by Prated, Pavailable or Pinstantaneous depending on PF_curve_type
|  |  |  | J+29 | 1 |  |  |  | PF_curve_P_2 | P-f curve active power points. Defined by 10 points. They are multiplied by Prated, Pavailable or Pinstantaneous depending on PF_curve_type
|  |  |  | J+30 | 1 |  |  |  | PF_curve_P_3 | P-f curve active power points. Defined by 10 points. They are multiplied by Prated, Pavailable or Pinstantaneous depending on PF_curve_type
|  |  |  | J+31 | 0 |  |  |  | PF_curve_P_4 | P-f curve active power points. Defined by 10 points. They are multiplied by Prated, Pavailable or Pinstantaneous depending on PF_curve_type
|  |  |  | J+32 | 0 |  |  |  | PF_curve_P_5 | P-f curve active power points. Defined by 10 points. They are multiplied by Prated, Pavailable or Pinstantaneous depending on PF_curve_type
|  |  |  | J+33 | 0 |  |  |  | PF_curve_P_6 | P-f curve active power points. Defined by 10 points. They are multiplied by Prated, Pavailable or Pinstantaneous depending on PF_curve_type
|  |  |  | J+34 | -0.95 |  |  |  | PF_curve_P_7 | P-f curve active power points. Defined by 10 points. They are multiplied by Prated, Pavailable or Pinstantaneous depending on PF_curve_type
|  |  |  | J+35 | -0.95 |  |  |  | PF_curve_P_8 | P-f curve active power points. Defined by 10 points. They are multiplied by Prated, Pavailable or Pinstantaneous depending on PF_curve_type
|  |  |  | J+36 | -0.95 |  |  |  | PF_curve_P_9 | P-f curve active power points. Defined by 10 points. They are multiplied by Prated, Pavailable or Pinstantaneous depending on PF_curve_type
|  |  |  | J+37 | -0.95 |  |  |  | PF_curve_P_10 | P-f curve active power points. Defined by 10 points. They are multiplied by Prated, Pavailable or Pinstantaneous depending on PF_curve_type
|  |  |  | J+38 | -0.022222 |  |  |  | PFC_RRL_negative | Active power maximum falling ramp for 1 WTG for P-f control mode. By default, -100kW/s.
|  |  |  | J+39 | 0.016667 |  |  |  | PFC_RRL_positive | Active power maximum rising ramp for 1 WTG for P-f control mode. By default, 75kW/s.
|  |  |  | J+40 | -0.95 |  |  |  | PFP_curve_cosphi_1 | cosphi values in PCC for cosphi_P control mode. Cap = +, Ind = -.
|  |  |  | J+41 | -0.95 |  |  |  | PFP_curve_cosphi_2 | cosphi values in PCC for cosphi_P control mode. Cap = +, Ind = -.
|  |  |  | J+42 | -0.95 |  |  |  | PFP_curve_cosphi_3 | cosphi values in PCC for cosphi_P control mode. Cap = +, Ind = -.
|  |  |  | J+43 | 1 |  |  |  | PFP_curve_cosphi_4 | cosphi values in PCC for cosphi_P control mode. Cap = +, Ind = -.
|  |  |  | J+44 | 1 |  |  |  | PFP_curve_cosphi_5 | cosphi values in PCC for cosphi_P control mode. Cap = +, Ind = -.
|  |  |  | J+45 | 1 |  |  |  | PFP_curve_cosphi_6 | cosphi values in PCC for cosphi_P control mode. Cap = +, Ind = -.
|  |  |  | J+46 | 0.95 |  |  |  | PFP_curve_cosphi_7 | cosphi values in PCC for cosphi_P control mode. Cap = +, Ind = -.
|  |  |  | J+47 | 0.95 |  |  |  | PFP_curve_cosphi_8 | cosphi values in PCC for cosphi_P control mode. Cap = +, Ind = -.
|  |  |  | J+48 | 0.95 |  |  |  | PFP_curve_cosphi_9 | cosphi values in PCC for cosphi_P control mode. Cap = +, Ind = -.
|  |  |  | J+49 | 0 |  |  |  | PFP_curve_P_1 | P (pu in WFbase) values for cosphi_P control mode. Values between 0 and 1, in increasing order.
|  |  |  | J+50 | 0.05 |  |  |  | PFP_curve_P_2 | P (pu in WFbase) values for cosphi_P control mode. Values between 0 and 1, in increasing order.
|  |  |  | J+51 | 0.1 |  |  |  | PFP_curve_P_3 | P (pu in WFbase) values for cosphi_P control mode. Values between 0 and 1, in increasing order.
|  |  |  | J+52 | 0.45 |  |  |  | PFP_curve_P_4 | P (pu in WFbase) values for cosphi_P control mode. Values between 0 and 1, in increasing order.
|  |  |  | J+53 | 0.5 |  |  |  | PFP_curve_P_5 | P (pu in WFbase) values for cosphi_P control mode. Values between 0 and 1, in increasing order.
|  |  |  | J+54 | 0.97 |  |  |  | PFP_curve_P_6 | P (pu in WFbase) values for cosphi_P control mode. Values between 0 and 1, in increasing order.
|  |  |  | J+55 | 0.98 |  |  |  | PFP_curve_P_7 | P (pu in WFbase) values for cosphi_P control mode. Values between 0 and 1, in increasing order.
|  |  |  | J+56 | 0.99 |  |  |  | PFP_curve_P_8 | P (pu in WFbase) values for cosphi_P control mode. Values between 0 and 1, in increasing order.
|  |  |  | J+57 | 1 |  |  |  | PFP_curve_P_9 | P (pu in WFbase) values for cosphi_P control mode. Values between 0 and 1, in increasing order.
|  |  |  | J+58 | 0.05 |  |  |  | Pmin_WF | Minimum value of the Pref to the WTGs
|  |  |  | J+59 | 0.045 |  |  |  | QControl_k_PI | Q controller proportional gain. Should be tuned depending on WF_WTG, SCR, losses.
|  |  |  | J+60 | 222.2222 |  |  |  | QControl_slope_q_ref | Maximum ramp rate of Parks Q reference for Qdirect control. Standard Value = 300kVAr/s * WF_WTG.
|  |  |  | J+61 | 0.06 |  |  |  | QControl_T_PI | Q controller time constant.
|  |  |  | J+62 | 1350 |  |  |  | QDistPushBand | Q Push Band to apply Fast or Slow ramp. Defined in % of Qbase in RCC.
|  |  |  | J+63 | 675 |  |  |  | QDistS1FastRamp | Fast ramp for Q. Defined in %/s of Qbase in RCC.
|  |  |  | J+64 | 337.5 |  |  |  | QDistS1SlowRamp | Slow ramp for Q. Defined in %/s of Qbase in RCC.
|  |  |  | J+65 | 67.5 |  |  |  | QDistS2Ramp | Maximum Q ramp in Step 2 to compensate Q among the different technologies. Defined in % of Qbase in RCC.
|  |  |  | J+66 | 5 |  |  |  | QDistSecondsInStep2Band | Time inside the band to pass to Step 2.
|  |  |  | J+67 | 100 |  |  |  | QDistSpBand | Q Band for changing from Step1 to Step2. Defined in % of Qbase in RCC.
|  |  |  | J+68 | 0.01 |  |  |  | QDistVSpBand | V Band for changing from Step1 to Step2. Defined in % in RCC.
|  |  |  | J+69 | 1000 |  |  |  | Qref_WP_max | Maximum Q capability of the Park
|  |  |  | J+70 | 10 |  |  |  | ReactCycleMult | Number of cycles to repeat Qsetpoint for all the control modes except Vdirect.
|  |  |  | J+71 | 135 |  |  |  | ReactCycleMultBandSize | Q Band for the use of the Cycle Multiplier. Defined in % of Qbase in RCC.
|  |  |  | J+72 | 5 |  |  |  | ReactVCycleMult | Number of cycles to repeat Qsetpoint for Vdirect.
|  |  |  | J+73 | 0.0044 |  |  |  | ReactVCycleMultBandSize | V Band for the use of the Cycle Multiplier. Defined in % in RCC.
|  |  |  | J+74 | 0.0044 |  |  |  | ReactVoltageBandSize | V Push Band to apply Fast or Slow ramp. Defined in % in RCC (kV).
|  |  |  | J+75 | 337.5 |  |  |  | ReactVoltageFastRamp | Q Fast ramp for Vdirect. Defined in %/s of Qbase in RCC.
|  |  |  | J+76 | 135 |  |  |  | ReactVoltageSlowRamp | Q Slow ramp for Vdirect. Defined in %/s of Qbase in RCC.
|  |  |  | J+77 | 0.00066 |  |  |  | ReactVoltageRampSmooth | Smooth Band applied to the Qramps for Vdirect
|  |  |  | J+78 | 2.1 |  |  |  | Ti_APC_P | APC controller integral time constant.
|  |  |  | J+79 | 0.066667 |  |  |  | VControl_k_PI | Vdirect controller proportional gain. Should be tuned depending on WF_WTG, SCR, losses.
|  |  |  | J+80 | 0.01 |  |  |  | VControl_T_PI | Vdirect controller integrator time constant.
|  |  |  | J+81 | 0.85 |  |  |  | Vdip_on_threshold_PCC | POC voltage level to activate the WFR dip mode.
|  |  |  | J+82 | 0.9 |  |  |  | Vdip_off_threshold_PCC | POC voltage level to deactivate the WFR dip mode (after a delay of DipMaxTime_PCC).
|  |  |  | J+83 | 1.12 |  |  |  | Vov_on_threshold_PCC | POC voltage level to activate the WFR OV mode.
|  |  |  | J+84 | 1.1 |  |  |  | Vov_off_threshold_PCC | POC voltage level to deactivate the WFR OV mode (after a delay of OVMaxTime_PCC).
|  |  |  | J+85 | 0.1 |  |  |  | VQstatic_deadband | Voltage deadband used with VQ-static mode 3.
|  |  |  | J+86 | 0 |  |  |  | VQstatic_HighVband | Upper value for the voltage error deadband, used in VQ-static mode 2.
|  |  |  | J+87 | 0 |  |  |  | VQstatic_LowVband | Lower value for the voltage error deadband, used in VQ-static mode 2.
|  |  |  | J+88 | 23.2444 |  |  |  | VQstatic_q_max | VQ-static mode 2 curve: maximum Q reached // VQ-static mode 3 curve reactive power capacitive saturation limit = WF_WTG*sin(acos(0.95)).
|  |  |  | J+89 | -23.2444 |  |  |  | VQstatic_q_min | VQ-static mode 2 curve: minimum Q reached.
|  |  |  | J+90 | 1 |  |  |  | VQstatic_slope | Slope of Q vs Verror used in VQstatic mode 3.
|  |  |  | J+91 | 1.5 |  |  |  | VQstatic_Tfilt | Filter time constant for Qref_VQstatic.
|  |  |  | J+92 | 0.04 |  |  |  | VQstatic_V_maxQ | Voltage value at which VQstatic_q_max is reached in VQstatic mode 2.
|  |  |  | J+93 | -0.04 |  |  |  | VQstatic_V_minQ | Voltage value at which VQstatic_q_min is reached in VQstatic mode 2.
|  |  |  | J+94 | 0.31622 |  |  |  | WTG_Q_max | Maximum Qcap that each WTG can produce. From PQV matrix.
|  |  |  | J+95 | -0.31622 |  |  |  | WTG_Q_min | Maximum Qind that each WTG can produce (negative). From PQV matrix.
|  |  |  | J+96 | 1000 |  |  |  | WTG_Ramp_KVar_Rate | Ramp that dominates wind farm response over other features. Corresponds to 1 WTG.
|  |  |  | J+97 | 1 |  |  |  | WTGs_S1_Priority | Set to 1 for WTGs prioritization during Step 1 (Fast Response)
|  |  |  | J+98 | 1 |  |  |  | WTGs_S2_Priority | Set to 1 for WTGs prioritization during Step 2 (Steady State)